## Table
Menuitems | CAR0 | CAR | Rpo | Omegaop
Interior nonstructural walls and partitions; Light frame ≤ 9 ft (2.74 m) in height | 1 | 1 | 1.5 | 2
Interior nonstructural walls and partitions; Light frame > 9 ft (2.74 m) in height | 1 | 1 | 1.5 | 2
Interior nonstructural walls and partitions; Reinforced masonry | 1 | 1 | 1.5 | 2
Interior nonstructural walls and partitions; All other walls and partitions | 2.2 | 2.8 | 1.5 | 1.5
Cantilever elements (unbraced or braced to structural frame below its center of mass); Parapets and cantilever interior nonstructural walls | 1.8 | 2.2 | 1.5 | 1.75
Cantilever elements (unbraced or braced to structural frame below its center of mass); Chimneys where laterally braced or supported by the structural frame | 1.8 | 2.2 | 1.5 | 1.75
Cantilever elements (braced to structural frame above its center of mass); Parapets | 1 | 1 | 1.5 | 2
Cantilever elements (braced to structural frame above its center of mass); Chimneys | 1 | 1 | 1.5 | 2
Cantilever elements (braced to structural frame above its center of mass); Exterior nonstructural wallsb | 1 | 1 | 1.5 | 2
Exterior nonstructural wall elements and connectionsb; Wall element | 1 | 1 | 1.5 | 2
Exterior nonstructural wall elements and connectionsb; Body of wall panel connections | 1 | 1 | 1.5 | 2
Exterior nonstructural wall elements and connectionsb; Fasteners of the connecting system | 2.2 | 2.8 | 1.5 | 1
Veneer; Limited-deformability elements and attachments | 1 | 1 | 1.5 | 2
Veneer; Low-deformability elements and attachments | 1 | 1 | 1.5 | 2
Penthouses (except where framed by an extension of the building frame); Seismic force-resisting systems with R ≥ 6 | N/A | 1.4 | 2 | 2
Penthouses (except where framed by an extension of the building frame); Seismic force-resisting systems with 4 ≤ R < 6 | N/A | 2.2 | 2 | 1.75
Penthouses (except where framed by an extension of the building frame); Seismic force-resisting systems with R < 4 | N/A | 2.8 | 2 | 2.5
Penthouses (except where framed by an extension of the building frame); Other system | N/A | 2.8 | 1.5 | 1.5
Ceilings; All | 1 | 1 | 1.5 | 2
Cabinets; Permanent floor-supported storage cabinets more than 6 ft(1.8 m) tall, including contents | 1 | 1 | 1.5 | 2
Cabinets; Permanent floor-supported library shelving, book stacks, and bookshelves more than 6 ft (1.8 m) tall, including contents | 1 | 1 | 1.5 | 2
Laboratory equipment | 1 | 1 | 1.5 | 2
Access floors; Special access floors (designed in accordance with Section 13.5.7.2) | 1 | 1 | 2 | 2
Access floors; All other | 2.2 | 2.8 | 1.5 | 1.5
Appendages and ornamentations | 1.8 | 2.2 | 1.5 | 1.75
Signs and billboards | 1.8 | 2.2 | 1.5 | 1.75
Other rigid components | 1 | 1 | 1.5 | 2
Other flexible components; High-deformability elements and attachments | 1.4 | 1.4 | 1.5 | 2
Other flexible components; Limited-deformability elements and attachments | 1.8 | 2.2 | 1.5 | 1.75
Other flexible components; Low-deformability materials and attachments | 2.2 | 2.8 | 1.5 | 1.5
Egress stairways not part of the building seismic force-resisting system | 1 | 1 | 1.5 | 2
Egress stairs and ramp fasteners and attachments | 1.8 | 2.2 | 1.5 | 1.75
MECHANICAL AND ELECTRICAL COMPONENTS Air-side HVACR, fans, air handlers, air conditioning units, cabinet heaters, air distribution boxes, and other mechanical components constructed of sheet metal framing | 1.4 | 1.4 | 2 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Wet-side HVACR, boilers, furnaces, atmospheric tanks and bins, chillers, water heaters, heat exchangers, evaporators, air separators, manufacturing or process equipment, and other mechanical components … | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Air coolers (fin fans), air-cooled heat exchangers, condensing units, dry coolers, remote radiators, and other mechanical components elevated on integral structural steel or sheet metal supports | 1.8 | 2.2 | 1.5 | 1.75
MECHANICAL AND ELECTRICAL COMPONENTS Engines, turbines, pumps, compressors, and pressure vessels not supported on skirts and not within the scope of Chapter 15 | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Skirt-supported pressure vessels not within the scope of Chapter 15 Elevator and escalator components | 1.8 | 2.2 | 1.5 | 1.75
MECHANICAL AND ELECTRICAL COMPONENTS Elevator and escalator components | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Generators, batteries, inverters, motors, transformers, and other electrical components constructed of high-deformability materials | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Motor control centers, panel boards, switch gear, instrumentation cabinets, and other components constructed of sheet metal framing | 1.4 | 1.4 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Communication equipment, computers, instrumentation, and controls | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Roof-mounted stacks, cooling and electrical towers laterally braced below their center of mass | 1.8 | 2.2 | 1.5 | 1.75
MECHANICAL AND ELECTRICAL COMPONENTS Roof-mounted stacks, cooling and electrical towers laterally braced above their center of mass | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Lighting fixtures | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Other mechanical or electrical components | 1 | 1 | 1.5 | 2
MECHANICAL AND ELECTRICAL COMPONENTS Manufacturing or process conveyors (nonpersonnel) | 1.8 | 2.2 | 1.5 | 1.75
VIBRATION-ISOLATED COMPONENTS AND SYSTEMSa Components and systems isolated using neoprene elements and neoprene isolated floors with built-in or separate elastomeric snubbing devices or resilient perimeter stops | 1.8 | 2.2 | 1.3 | 1.75
VIBRATION-ISOLATED COMPONENTS AND SYSTEMSa Spring-isolated components and systems and vibration-isolated floors closely restrained using built-in or separate elastomeric snubbing devices or resilient perimeter stops | 1.8 | 2.2 | 1.3 | 1.75
VIBRATION-ISOLATED COMPONENTS AND SYSTEMSa Internally isolated components and systems | 1.8 | 2.2 | 1.3 | 1.75
VIBRATION-ISOLATED COMPONENTS AND SYSTEMSa Suspended vibration-isolated equipment, including in-line duct devices and suspended internally isolated components | 1.8 | 2.2 | 1.3 | 1.75
EQUIPMENT SUPPORT STRUCTURES AND PLATFORMS Support structures and platforms where Tp/Ta < 0.2, or Tp ≤ 0.06 s, per Section 13.6.4.6 | NA | 1 | 1.5 | 2
EQUIPMENT SUPPORT STRUCTURES AND PLATFORMS Seismic force-resisting systems with R > 3 | 1.4 | 1.4 | 1.5 | 2
EQUIPMENT SUPPORT STRUCTURES AND PLATFORMS Seismic force-resisting systems with R ≤ 3 | 1.8 | 2.2 | 1.5 | 1.75
EQUIPMENT SUPPORT STRUCTURES AND PLATFORMS Other systems | 2.2 | 2.8 | 1.5 | 1.5
DISTRIBUTION SYSTEM SUPPORTS Tension-only and cable bracing | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEM SUPPORTS Cold-formed steel rigid bracing | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEM SUPPORTS Hot-rolled steel bracing | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEM SUPPORTS Other rigid bracing | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEM SUPPORTS Lateral resistance provided by rods in flexure | 1.8 | 2.2 | 1.5 | 1.75
DISTRIBUTION SYSTEM SUPPORTS Vertical cantilever supports such as pipe tees and moment frames above and supported by a floor or roof | 1.8 | 2.2 | 1.5 | 1.75
DISTRIBUTION SYSTEMS Piping in accordance with ASME B31 (2001, 2002, 2008, 2010), including in-line components with joints made by welding or brazing | 1 | 1 | 3 | 2
DISTRIBUTION SYSTEMS Piping in accordance with ASME B31, including in-line components, constructed of high- or limited-deformability materials, with joints made by threading, bonding, compression couplings, or grooved couplings | 1 | 1 | 2 | 2
DISTRIBUTION SYSTEMS Piping and tubing not in accordance with ASME B31, including in-line components, constructed of high-deformability materials, with joints made by welding or brazing | 1 | 1 | 2 | 2
DISTRIBUTION SYSTEMS Piping and tubing not in accordance with ASME B31, including in-line components, constructed of high- or limited-deformability materials, with joints made by threading, bonding, compression couplings, or grooved couplings | 1.8 | 2.2 | 2 | 1.75
DISTRIBUTION SYSTEMS Piping and tubing constructed of low-deformability materials, such as cast iron, glass, and nonductile plastics | 1.8 | 2.2 | 1.5 | 1.75
DISTRIBUTION SYSTEMS Duct systems, including in-line components, constructed of high-deformability materials, with joints made by welding or brazing | 1 | 1 | 2 | 2
DISTRIBUTION SYSTEMS Duct systems, including in-line components, constructed of high- or limited-deformability materials, with joints made by means other than welding or brazing | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEMS Duct systems, including in-line components, constructed of low-deformability materials, such as cast iron, glass, and nonductile plastics | 1.8 | 2.2 | 1.5 | 1.75
DISTRIBUTION SYSTEMS Electrical conduit, cable trays, and raceways | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEMS Bus ducts | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEMS Plumbing | 1 | 1 | 1.5 | 2
DISTRIBUTION SYSTEMS Pneumatic tube transport systems | 1 | 1 | 1.5 | 2

## MyTables (hidden)
List - do not delete
List - do not delete |  | Yes |  | Risk Category |  |  | List - do not delete
A | 1 | No |  | I |  |  | A | 1
B | 2 |  |  | II |  |  | B Estimated 11.4.3
BC | 3 |  |  | III |  |  | B | 2
C | 4 |  |  | IV |  |  | C | 3
CD | 5 | [5 empty] | D | 4
D | 6 | [5 empty] | D Default 11.4.3 | 4
DE | 7 | [5 empty] | E | 5
E | 8
F | 9
|  | Fa | [10 empty] | Calculated Using Measured or Estimated Shear Wave Velocity Profile
|  |  |  | artificial lower value |  |  |  | for site class E interpolation |  |  | artificial upper value | NEHRP |  | ASCE 7-16
|  |  | SS | 0 | 0.25 | 0.5 | 0.75 | 0.99999 | 1 | 1.25 | 5 |  | Upper Limit |  | Upper Limit
|  |  | A | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | A | 100000 | A | 100000
|  |  | B | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | B | 5000 | B | 5001
|  |  | C | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | BC | 3000 | C | 2500
|  |  | D | 1.6 | 1.6 | 1.4 | 1.2 | 1.1 | 1.1 | 1 | 1 | C | 2100 | D | 1200
|  |  | E | 2.4 | 2.4 | 1.7 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | CD | 1450 | E | 600
[12 empty] | D | 1000
[12 empty] | DE | 700
|  | Fv | [9 empty] | E | 500
|  |  | S1 | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 5 | F
|  |  | A | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
|  |  | B | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
|  |  | C | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.4
|  |  | D | 2.4 | 2.4 | 2.2 | 2 | 1.9 | 1.8 | 1.7 | 1.7
|  |  | E | 4.2 | 4.2 | 3.3 | 2.8 | 2.4 | 2.2 | 2 | 2
|  | Cu |  | 0 | 0.1 | 0.15 | 0.2 | 0.3 | 0.4 | 5
|  |  |  | 1.7 | 1.7 | 1.6 | 1.5 | 1.4 | 1.4 | 1.4